## Cover
Whole of System Plan 2020
Assumptions book
2020-10-12
Reliance Restricted

## Change Log
Change Log
Version History
Version Number | Date | Description
1 | 2019-11-29 | First release of draft WOSP modelling assumptions.
2 | 2020-01-09 | Badgingarra Solar Farm added to Wind & solar planting list. East Rockingham Resource Recovery Facility added to Existing plant params.
3 | 2020-10-12 | Updated Base gas price in Fuel Prices GSOO.
Compressed air and pumped hydro storage technologies combined into one large-scale 'Storage' technology.
Storage moved from Bespoke new entrant params to New entrant params.
Bespoke new entrant params removed.
Flexible gas added to New entrant params.
Storage and Flexible gas added to Technology CAPEX.
Storage and Flexible gas added to Candidate technologies by zone.
Storage and Flexible gas added to Indicative LCOE comparisons.
CCGT and OCGT parameters updated in Technology CAPEX.
Battery - 2hrs and Battery - 4hrs parameters updated in New entrant params.
Battery - 2hrs and Battery - 4hrs parameters updated in Technology CAPEX.
Variable fuel transport cost ($/GJ) changed to Fuel transport cost ($/GJ) in Existing plant params.
Fuel transport cost ($/GJ) parameters updated.
Maintenance & forced outage statistics to be applied to all generators
Badgingarra Solar Farm added to Existing plant params.
Phoenix Kwinana and East Rockingham Resource Recovery Facility added to Thermal generator developments.
Station names updated in Existing plant params.

## Summary
Summary
Field | Value | Comments
Study start year | 2020-21
Study end year | 2039-40
Number of years | 20
Assumptions book dollars | Real 30 June 2019 AUD | Modelling began on 1 July 2019 with 30 June 2019 dollars and modelling was finalised 30 June 2020 and results reported in 30 June 2020 dollars
Reporting dollars | Real 30 June 2020 AUD

## Existing plant params
Existing plant params
[5 empty] | Source | AEMO Market Data | ETIU Foundation Market Parameters - Information Papers | 2020-21 AEMO Assignment of Capacity Credits | AEMO WEM Data Dashboard | AEMO WEM Data Dashboard | 2019-20 AEMO ISP | 2014-15 Margin Peak and Margin Off-Peak parameters |  | 2015-16 AEMO Generator emission factors | 2016-17 NGER | 2018 AEMO ISP
[5 empty] | URL | http://data.wa.aemo.com.au/#facilities | https://www.wa.gov.au/sites/default/files/2019-08/Information-Paper-Foundation-Market-Parameters.pdf | https://www.aemo.com.au/Electricity/Wholesale-Electricity-Market-WEM/Reserve-capacity-mechanism/Assignment-of-capacity-credits | https://www.aemo.com.au/Electricity/Wholesale-Electricity-Market-WEM/Data-dashboard#generation-facilities | https://www.aemo.com.au/Electricity/Wholesale-Electricity-Market-WEM/Data-dashboard#generation-facilities | Values are from NEM facilities of the same technology type. Biomass/landfill gas FOM from 2018 ISP, converted to real June 2019 AUD using CPI. | https://www.erawa.com.au/electricity/wholesale-electricity-market/ancillary-services-parameters/spinning-reserve-margin_peak-and-margin_off-peak/margin-peak-and-margin-off-peak-parameters-for-201415 |  | https://www.aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/NTNDP/2016/Data_Sources/ACIL-ALLEN---AEMO-Emission-factors-20160511.xlsx | http://www.cleanenergyregulator.gov.au/NGER/National%20greenhouse%20and%20energy%20reporting%20data/electricity-sector-emissions-and-generation-data/electricity-sector-emissions-and-generation-data-2016-17 | Values are from NEM facilities of the same technology type
Facility code | Station name | Participant Group | zone | Fuel type | Plant type | Nameplate capacity (MW) | Loss factors - Southern Terminal reference zone | Capacity credits | Ramp rate down (MW/min) | Ramp rate up (MW/min) | FOM ($/MW nameplate, Real June 2019 AUD) | VOM ($/MWh sent-out, Real June 2019 AUD) | Fuel transport cost ($/GJ) | Fugitive EI (t CO2-e/MWh as generated) | Combustion EI (t CO2-e/MWh as generated) | Auxiliary factor/self load (%)
ALCOA_WGP | Alcoa Wagerup | Alcoa | SW | Cogeneration | Cogeneration | 26 | 0.9638 | 26 | 3 | 3 | 10670 | 2.5737 | 1.6927 | 0.055115 | 0.6 | 3%
ALINTA_PNJ_U1 | Alinta Pinjarra 1 | Alinta | SW | Natural gas | Cogeneration | 143 | 0.9554 | 137 | 9.4 | 9.4 | 10670 | -22.5328 | 1.6927 | 0.055115 | 0.66 | 3%
ALINTA_PNJ_U2 | Alinta Pinjarra 2 | Alinta | SW | Natural gas | Cogeneration | 143 | 0.9554 | 137 | 9.4 | 9.4 | 10670 | -22.5328 | 1.6927 | 0.055115 | 0.66 | 3%
ALINTA_WGP_GT | Alinta Wagerup Gas Turbine 1 | Alinta | SW | Natural gas | OCGT | 195.152 | 0.9862 | 196 | 8 | 8 | 15130 | 2.7445 | 1.6927 | 0.04776 | 0.65 | 1%
ALINTA_WGP_U2 | Alinta Wagerup Gas Turbine 2 | Alinta | SW | Natural gas | OCGT | 210 | 0.9862 | 196 | 8 | 8 | 15130 | 2.7445 | 1.6927 | 0.04776 | 0.65 | 1%
BW1_BLUEWATERS_G2 | Bluewaters 1 | Bluewaters | SW | Black coal | Black coal | 217 | 0.9782 | 217 | 2 | 2 | 54050 | 2.563 | 1.6927 | 0.023718 | 0.89 | 8%
BW2_BLUEWATERS_G1 | Bluewaters 2 | Bluewaters | SW | Black coal | Black coal | 217 | 0.9782 | 217 | 2 | 2 | 54050 | 2.563 | 1.6927 | 0.023125 | 0.87 | 8%
COCKBURN_CCG1 | Cockburn CCGT | Synergy | MS | Natural gas | CCGT | 249.7 | 1.0083 | 240 | 12 | 12 | 10670 | 4.4318 | 1.6927 | 0.030889 | 0.39 | 3%
COLLIE_G1 | Collie G1 | Synergy | SW | Black coal | Black coal | 318.3 | 0.9739 | 317.2 | 4 | 4 | 54050 | 1.2815 | 1.6927 | 0.024379 | 0.9 | 8%
TESLA_PICTON_G1 | Tesla Picton | Tesla | SW | Distillate | Diesel engine | 9.9 | 0.97734 | 9.9 | 2 | 2 | 15130 | 2.9581 | 1.6927 | 0.042984 | 0.83819 | 1%
KEMERTON_GT11 | Kemerton 1 | Synergy | SW | Natural gas | OCGT | 155 | 0.9814 | 155 | 15 | 15 | 15130 | 2.7445 | 1.6927 | 0.04776 | 0.67 | 1%
KEMERTON_GT12 | Kemerton 2 | Synergy | SW | Natural gas | OCGT | 155 | 0.9814 | 155 | 15 | 15 | 15130 | 2.7445 | 1.6927 | 0.04776 | 0.67 | 1%
KWINANA_GT2 | Kwinana Gas Turbine 2 | Synergy | MS | Natural gas | OCGT | 103.2 | 1.0062 | 98.5 | 30 | 30 | 15130 | 7.3045 | 1.6927 | 0.038208 | 0.54 | 1%
KWINANA_GT3 | Kwinana Gas Turbine 3 | Synergy | MS | Natural gas | OCGT | 103.2 | 1.0062 | 99.2 | 30 | 30 | 15130 | 7.3045 | 1.6927 | 0.038208 | 0.54 | 1%
PPP_KCP_EG1 | Kwinana EG1 | Synergy | MS | Cogeneration | Cogeneration | 85.7 | 1.0077 | 80.4 | 1 | 1 | 10670 | 5.2114 | 1.6927 | 0.037137 | 0.55 | 3%
PERTHENERGY_KWINANA_GT1 | Kwinana Swift OCGT | Perth Energy | MS | Natural gas | OCGT | 116 | 1.0017 | 109 | 6 | 6 | 15130 | 12.3664 | 1.6927 | 0.050914 | 0.58 | 1%
MUJA_G5 | Muja 5 | Synergy | SW | Black Coal | Black coal | 195.8 | 0.9773 | 195 | 4 | 4 | 54050 | 5.1366 | 1.6927 | 0.025734 | 0.92 | 8%
MUJA_G6 | Muja 6 | Synergy | SW | Black Coal | Black coal | 195.8 | 0.9773 | 193 | 4 | 4 | 54050 | 5.1366 | 1.6927 | 0.025734 | 0.92 | 8%
MUJA_G7 | Muja 7 | Synergy | SW | Black Coal | Black coal | 212.6 | 0.9773 | 211 | 4 | 4 | 54050 | 4.8269 | 1.6927 | 0.024955 | 0.92 | 8%
MUJA_G8 | Muja 8 | Synergy | SW | Black Coal | Black coal | 212.6 | 0.9773 | 211 | 4 | 4 | 54050 | 4.8269 | 1.6927 | 0.024955 | 0.92 | 8%
NAMKKN_MERR_SG1 | Merredin Gas Turbine | Merredin Energy | ME | Distillate | Diesel engine | 92.6 | 0.938 | 82 | 6 | 6 | 15130 | 5.2755 | 1.6927 | 0.042768 | 1.07 | 1%
NEWGEN_KWINANA_CCG1 | Kwinana Combined Cycle Gas | Sumitomo | MS | Natural gas | CCGT | 335 | 0.9993 | 327.8 | 6 | 6 | 10670 | 2.563 | 1.6927 | 0.030348 | 0.39 | 3%
NEWGEN_NEERABUP_GT1 | Neerabup Gas Turbine 1 | ERM | NB | Natural gas | OCGT | 342 | 1.0066 | 330.6 | 11 | 11 | 15130 | 2.7445 | 1.6927 | 0.050914 | 0.62 | 1%
PRK_AG | Parkeston | GPPL | EG | Natural gas | OCGT | 68 | 1.1332 | 59.4 | 3 | 3 | 15130 | 5.2007 | 1.7056 | 0.046219 | 0.58 | 1%
PINJAR_GT1 | Pinjar Gas Turbine 1 | Synergy | NB | Natural gas | OCGT | 38.5 | 1.0139 | 30.7 | 8 | 8 | 15130 | 2.9581 | 1.6927 | 0.065127 | 0.82 | 1%
PINJAR_GT2 | Pinjar Gas Turbine 2 | Synergy | NB | Natural gas | OCGT | 38.5 | 1.0139 | 30.3 | 8 | 8 | 15130 | 2.9581 | 1.6927 | 0.065127 | 0.82 | 1%
PINJAR_GT3 | Pinjar Gas Turbine 3 | Synergy | NB | Natural gas | OCGT | 39.3 | 1.0139 | 37 | 8 | 8 | 15130 | 2.9581 | 1.6927 | 0.065127 | 0.82 | 1%
PINJAR_GT4 | Pinjar Gas Turbine 4 | Synergy | NB | Natural gas | OCGT | 39.3 | 1.0139 | 37 | 8 | 8 | 15130 | 2.9581 | 1.6927 | 0.065127 | 0.82 | 1%
PINJAR_GT5 | Pinjar Gas Turbine 5 | Synergy | NB | Natural gas | OCGT | 39.3 | 1.0139 | 37 | 8 | 8 | 15130 | 2.9581 | 1.6927 | 0.065127 | 0.82 | 1%
PINJAR_GT7 | Pinjar Gas Turbine 7 | Synergy | NB | Natural gas | OCGT | 39.3 | 1.0139 | 37 | 8 | 8 | 15130 | 2.9581 | 1.6927 | 0.065127 | 0.82 | 1%
PINJAR_GT9 | Pinjar Gas Turbine 9 | Synergy | NB | Natural gas | OCGT | 118.2 | 1.0139 | 111 | 10 | 10 | 15130 | 5.1366 | 1.6927 | 0.0597 | 0.82 | 1%
PINJAR_GT10 | Pinjar Gas Turbine 10 | Synergy | NB | Natural gas | OCGT | 118.2 | 1.0139 | 111 | 10 | 10 | 15130 | 5.1366 | 1.6927 | 0.0597 | 0.82 | 1%
PINJAR_GT11 | Pinjar Gas Turbine 11 | Synergy | NB | Natural gas | OCGT | 130 | 1.0139 | 124 | 10 | 10 | 15130 | 5.9803 | 1.6927 | 0.057312 | 0.82 | 1%
STHRNCRS_EG | Southern Cross Power Station | TransAlta | EG | Natural gas | OCGT | 23 | 1.1442 | 20 | 3 | 3 | 15130 | 2.7445 | 1.7056 | 0.051581 | 0.55 | 1%
TESLA_GERALDTON_G1 | Tesla Geraldton | Tesla | NC | Distillate | Diesel engine | 9.9 | 0.97654 | 9.9 | 2 | 2 | 15130 | 2.9581 | 1.6927 | 0.042984 | 0.83819 | 1%
TESLA_KEMERTON_G1 | Tesla Kemerton | Tesla | SW | Distillate | Diesel engine | 9.9 | 0.96398 | 9.9 | 2 | 2 | 15130 | 2.9581 | 1.6927 | 0.042984 | 0.83819 | 1%
TESLA_NORTHAM_G1 | Tesla Northam | Tesla | ME | Distillate | Diesel engine | 9.9 | 1.0298 | 9.9 | 2 | 2 | 15130 | 2.9581 | 1.6927 | 0.042984 | 0.83819 | 1%
TIWEST_COG1 | Tiwest | TiWest | MS | Cogeneration | Cogeneration | 42.1 | 1.0054 | 36 | 3 | 3 | 10670 | 2.5737 | 1.6927 | 0.04891 | 0.63009 | 3%
BIOGAS01 | CleanTech Biogas | CleanTech Energy | MT | Waste | OCGT | 2 | 1 | 1.551 | 1 | 0 | 131548 | 8.6714 | - | 0 | 0.04819 | 8%
HENDERSON_RENEWABLE_IG1 | Henderson Landfill Gas | Waste Gas Resources | MT | Landfill gas | OCGT | 3 | 1 | 1.761 | 0.5 | 0 | 131548 | 8.6714 | - | 0 | 0.069552 | 8%
KALAMUNDA_SG | Kalamunda | Landfill Gas and Power | MT | Landfill gas | OCGT | 1.3 | 1 | 1.3 | 0.6 | 0.6 | 131548 | 8.6714 | - | 0 | 0.23 | 8%
RED_HILL | Red Hill | Landfill Gas and Power | MT | Landfill gas | OCGT | 3.64 | 1 | 2.868 | 0.6 | 0 | 131548 | 8.6714 | - | 0 | 0.06 | 8%
ROCKINGHAM | Rockingham | Perth Energy | MS | Landfill gas | OCGT | 4 | 1 | 2.286 | 0.3 | 0 | 131548 | 8.6714 | - | 0 | 0.05 | 8%
SOUTH_CARDUP | South Cardup | Perth Energy | MT | Landfill gas | OCGT | 4.158 | 1 | 3.009 | 0.3 | 0 | 131548 | 8.6714 | - | 0 | 0.06 | 8%
TAMALA_PARK | Tamala Park | Landfill Gas and Power | NB | Landfill gas | OCGT | 4.8 | 1 | 4.292 | 0.6 | 0 | 131548 | 8.6714 | - | 0 | 0.06 | 8%
PHOENIX_KWINANA_WTE_G1 | Phoenix Kwinana | Kwinana WTE Project Co | MS | Municipal waste | Steam turbine | 36 | 1.0044 | 33 | 6 | 6 | 131548 | 0 | - | 0 | 1.4425 | 8%
East Rockingham Resource Recovery Facility | East Rockingham Resource Recovery Facility | ACCIONA, HZI, John Laing | MS | Municipal waste | Steam turbine | 28.9 | 1.0044 | 26.5 | 4.8 | 4.8 | 131548 | 0 | - | 0 | 1.4425 | 8%
NORTHAM_SF_PV1 | Northam Solar Farm | Northam Solar Project Partnership | ME | Solar | Solar PV | 9.8 | 1.0373 | 2.568 | 1 | 0 | 26110 | 0 | - | 0 | 0 | 0%
Emu Downs Solar Farm | Emu Downs Solar Farm | APA | MW | Solar | Solar PV | 20 | 0.9985 | 4.12 | 2 | 0 | 26110 | 0 | - | 0 | 0 | 0%
GREENOUGH_RIVER_PV1 | Greenough River Solar Farm | GRSF Trust | NC | Solar | Solar PV | 10 | 0.9743 | 1.995 | 2 | 0 | 26110 | 0 | - | 0 | 0 | 0%
AMBRISOLAR_PV1 | Ambrisolar | Metro Power | ME | Solar | Solar PV | 0.96 | 1 | 0.27 | 0.2 | 0 | 26110 | 0 | - | 0 | 0 | 0%
GREENOUGH_RIVER_PV1_UPG_1 | Greenough River Solar Farm Upgrade | GRSF Trust | NC | Solar | Solar PV | 30 | 0.9743 | 7.91 | 6 | 0 | 26110 | 0 | - | 0 | 0 | 0%
MERSOLAR_PV1 | Merredin Solar Farm | Rizen | ME | Solar | Solar PV | 100 | 0.99 | 35.64 | 26.4 | 0 | 26110 | 0 | - | 0 | 0 | 0%
Badgingarra Solar Farm | Badgingarra Solar Farm | Alinta | MW | Solar | Solar PV | 17.5 | 0.9985 | 0 | 2 | 0 | 26110 | 0 | - | 0 | 0 | 0%
ALINTA_WWF | Walkaway Wind Farm | Alinta | NC | Wind | Wind | 89.1 | 0.9244 | 22.035 | 89 | 0 | 45820 | 0 | - | 0 | 0 | 0%
BADGINGARRA_WF1 | Badgingarra | Alinta | MW | Wind | Wind | 130 | 0.9985 | 36.428 | 20 | 0 | 45820 | 0 | - | 0 | 0 | 0%
BLAIRFOX_KARAKIN_WF1 | Karakin Wind Farm | Blair Flox | MW | Wind | Wind | 5 | 1.0054 | 0.736 | 5 | 0 | 45820 | 0 | - | 0 | 0 | 0%
BREMER_BAY_WF1 | Bremer Bay | Synergy | SE | Wind | Wind | 0.6 | 1.3752 | 0.19 | 2.4 | 0 | 45820 | 0 | - | 0 | 0 | 0%
DCWL_DENMARK_WF1 | Denmark Wind Farm | Denmark Community Windfarm | SE | Wind | Wind | 1.44 | 1.3682 | 0.414 | 0.2 | 0 | 45820 | 0 | - | 0 | 0 | 0%
EDWFMAN_WF1 | Emu Downs | APA | MW | Wind | Wind | 80 | 0.9985 | 22.19 | 2 | 0 | 45820 | 0 | - | 0 | 0 | 0%
GRASMERE_WF1 | Grasmere Wind Farm | AGWF Trust | SE | Wind | Wind | 13.8 | 0.99665 | 4.329 | 10 | 0 | 45820 | 0 | - | 0 | 0 | 0%
INVESTEC_COLLGAR_WF1 | Collgar Wind Farm | Collgar | ME | Wind | Wind | 206 | 0.9849 | 22.894 | 33 | 0 | 45820 | 0 | - | 0 | 0 | 0%
KALBARRI_WF1 | Kalbarri Wind Farm | Synergy | NC | Wind | Wind | 1.6 | 1 | 0.287 | 3.6 | 0 | 45820 | 0 | - | 0 | 0 | 0%
MWF_MUMBIDA_WF1 | Mumbida Wind Farm | Mumbida Wind Farm | NC | Wind | Wind | 55 | 0.9326 | 8.943 | 8 | 0 | 45820 | 0 | - | 0 | 0 | 0%
SKYFRM_MTBARKER_WF1 | Mount Barker Wind Farm | Mt.Barker Power Company | SE | Wind | Wind | 2.43 | 1 | 0.606 | 0.9 | 0 | 45820 | 0 | - | 0 | 0 | 0%
ALBANY_WF1 | Albany Wind Farm | Synergy | SE | Wind | Wind | 21.6 | 0.99665 | 6.6 | 86 | 0 | 45820 | 0 | - | 0 | 0 | 0%
WARRADARGE_WF1 | Warradarge Wind Farm | Synergy | MW | Wind | Wind | 180 | 0.975 | 36.124 | 27.9 | 0 | 45820 | 0 | - | 0 | 0 | 0%
YANDIN_WF1 | Yandin Wind Farm | Alinta | MW | Wind | Wind | 214.2 | 0.975 | 40.932 | 33.2 | 0 | 45820 | 0 | - | 0 | 0 | 0%
BLAIRFOX_BEROSRD_WF1 | Beros Road Wind Farm | Blair Fox | MW | Wind | Wind | 9.252 | 1 | 0 | 1.53 | 0 | 45820 | 0 | - | 0 | 0 | 0%
BLAIRFOX_WESTHILLS_WF3 | West Hills Wind Farm | Blair Fox | MW | Wind | Wind | 5 | 1.0054 | 0 | 5 | 0 | 45820 | 0 | - | 0 | 0 | 0%

## Thermal generator developments
Announced and suggested capacity developments
Based on public announcements. Further new entrants or retirements may be implemented based on simulation outcomes.
Technology Type | Maximum asset life
Black Coal | 50
OCGT | 40
Liquid | 35
Cogeneration | 40
Additions
Station | Capacity (MW) | Tech | Commissioning date
Phoenix Kwinana | 36 | Waste to energy | 2022-07-01
East Rockingham Resource Recovery Facility | 28.9 | Waste to energy | 2023-07-01
Retirements
Station name | Capacity (MW) | Tech | Age-based retirement date | Comments
Muja 5 | 195.8 | Black Coal | 2022-10-01 | https://www.mediastatements.wa.gov.au/Pages/McGowan/2019/08/Muja-Power-Station-in-Collie-to-be-scaled-back-from-2022.aspx
Muja 6 | 195.8 | Black Coal | 2024-10-01
Muja 7 | 212.6 | Black Coal | 2036-07-01 | Calculations based on asset life defined with reference to the current age of the asset.
MUJA_G8 | 212.6 | Black Coal | 2036-07-01
Pinjar GT's 1-7 | 234.2 | OCGT | 2030-07-01
Tiwest | 42.1 | Cogeneration | 2030-07-01
Parkeston | 68 | OCGT | 2036-07-01
Southern Cross Power Station | 23 | OCGT | 2036-07-01
Pinjar Gas Turbine 9 | 118.2 | OCGT | 2036-07-01
Pinjar Gas Turbine 10 | 118.2 | OCGT | 2036-07-01
Pinjar Gas Turbine 11 | 130 | OCGT | 2036-07-01
Kwinana EG1 | 85.7 | Cogeneration | 2036-07-01

## Wind & solar planting list
List of existing and commissioning wind and solar projects to be included in the modelling
List based on updated information provided through available market data and information
Assumed capacity factors based on historical data for existing projects. For new entrants, capacity factors are indicative and are assumed.
Facility code | Commissioning date | Project name | Capacity (MW) | zone | Technology | Capacity factor
GREENOUGH_RIVER_PV1 | Existing | Greenough River | 10 | NC | Tilted Plate PV | 25%
AMBRISOLAR_PV1 | Existing | Ambrisolar Solar Farm | 0.96 | ME | Single axis tracking PV | 30%
Emu Downs Solar Farm | Existing | Emu Downs Solar Farm | 20 | MW | Single axis tracking PV | 30%
Badgingarra Solar Farm | Existing | Badgingarra Solar Farm | 17.5 | MW | Single axis tracking PV | 30%
NORTHAM_SF_PV1 | Existing | Northam | 9.8 | ME | Single axis tracking PV | 30%
ALBANY_WF1 | Existing | Albany | 21.6 | SE | Wind turbine | 31%
BADGINGARRA_WF1 | Existing | Badgingarra | 130 | MW | Wind turbine | 46%
BREMER_BAY_WF1 | Existing | Bremer Bay | 0.6 | SE | Wind turbine | 31%
INVESTEC_COLLGAR_WF1 | Existing | Collgar | 206 | ME | Wind turbine | 37%
DCWL_DENMARK_WF1 | Existing | Denmark | 1.44 | SE | Wind turbine | 41%
EDWFMAN_WF1 | Existing | Emu Downs | 80 | MW | Wind turbine | 35%
GRASMERE_WF1 | Existing | Grasmere | 13.8 | SE | Wind turbine | 33%
KALBARRI_WF1 | Existing | Kalbarri | 1.6 | NC | Wind turbine | 41%
BLAIRFOX_KARAKIN_WF1 | Existing | Karakin | 5 | MW | Wind turbine | 35%
SKYFRM_MTBARKER_WF1 | Existing | Mt Barker | 2.43 | SE | Wind turbine | 41%
MWF_MUMBIDA_WF1 | Existing | Mumbida | 55 | NC | Wind turbine | 39%
ALINTA_WWF | Existing | Walkaway | 89.1 | NC | Wind turbine | 42%
BLAIRFOX_BEROSRD_WF1 | Existing | Beros Road | 9.252 | MW | Wind turbine | 46%
BLAIRFOX_WESTHILLS_WF3 | Existing | West Hills | 5 | MW | Wind turbine | 35%
GREENOUGH_RIVER_PV1_UPG_1 | 2020-07-01 | Greenough River 2 | 30 | NC | Single axis tracking PV | 30%
MERSOLAR_PV1 | 2020-07-01 | Merredin Solar Farm | 100 | ME | Single axis tracking PV | 30%
WARRADARGE_WF1 | 2020-07-01 | Warradarge | 180 | MW | Wind turbine | 46%
YANDIN_WF1 | 2020-07-01 | Yandin | 214.2 | MW | Wind turbine | 46%

## Maintenance & outages
Maintenance & forced outage statistics to be applied to all generators
Source: 2019 AEMO ISP input and assumptions workbook
Technology | Full outage rate | Partial outage rate | Full outage - mean time to repair (hrs) | Partial outage - mean time to repair (hrs) | Partial outage derating factor | Time on planned maintenance | Equivalent average days per year on planned maintenance | Comment
Black coal | 4.3% | 23.84% | 104 | 17 | 17.51% | 5.479% | 20 | Using Black Coal NSW profile
CCGT | 1.73% | 0.19% | 23 | 29 | 0.3652% | 5.479% | 20 | -
OCGT | 1.26% | 0.35% | 7 | 40 | 11.96% | 1.37% | 5 | -
Small OCGT (<150 MW) | 3.52% | 0.39% | 16 | 35 | 7.18% | 1.37% | 5 | -
Diesel | 3.52% | 0.39% | 16 | 35 | 7.18% | 1.644% | 6 | -
Cogeneration | 1.73% | 0.19% | 23 | 29 | 0.3652% | 5.479% | 20 | Using CCGT profile

## Gas Prices
Gas fuel costs for new contracts
Real June 2019 AUD
Gas prices ($/GJ) |  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | Sources
| High | 9.2373 | 9.7749 | 10.164 | 10.4815 | 10.7734 | 11.0448 | 11.1984 | 11.4984 | 11.7909 | 11.9984 | 12.1593 | 12.2909 | 12.4021 | 12.4984 | 12.5833 | 12.6593 | 12.7281 | 12.7909 | 12.8486 | 12.9021 | Gas Statement of Opportunities - December 2017, AEMO. https://www.aemo.com.au/-/media/Files/Gas/National_Planning_and_Forecasting/WA_GSOO/2017/2017-WA-GSOO.pdf
| Base | 5.9162 | 6.0698 | 6.3258 | 6.4794 | 6.5306 | 6.5818 | 6.6331 | 6.6843 | 6.7355 | 6.7355 | 6.7867 | 6.8379 | 7.5547 | 8.2716 | 8.2716 | 8.2716 | 8.2716 | 8.2716 | 8.2716 | 8.2716 | AEMO Wholesale, Delivered Gas Price Scenarios ¦ 2018 - 2040, Core Energy & Resources, January 2019. https://aemo.com.au/-/media/files/gas/national_planning_and_forecasting/gsoo/2019/core-eastern-australia-gas-price-projections-databook_16-january-2019.xlsx
| Low | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | 4.0963 | Gas Statement of Opportunities - December 2017, AEMO. https://www.aemo.com.au/-/media/Files/Gas/National_Planning_and_Forecasting/WA_GSOO/2017/2017-WA-GSOO.pdf

## Technology CAPEX
Capital costs for new technologies excluding connection costs
Real June 2019 AUD/MW
Source: | 2019 and 2020 AEMO ISP Input and Assumptions workbook adjusted for WA inputs and pricing in recent developments and WA Market participants and developers
Technology | WOSP scenario | Build Cost | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Battery - 2hrs | Groundhog Day | Expected | 1145800 | 1109000 | 1087100 | 1072100 | 1054400 | 853900 | 736600 | 662900 | 613800 | 583800 | 512900 | 510100 | 507400 | 504700 | 503300 | 500600 | 497900 | 496500 | 495100 | 492400
Battery - 2hrs | Cast Away | Expected | 1145800 | 1109000 | 1087100 | 1072100 | 1054400 | 853900 | 736600 | 662900 | 613800 | 583800 | 512900 | 510100 | 507400 | 504700 | 503300 | 500600 | 497900 | 496500 | 495100 | 492400
Battery - 2hrs | Techtopia | Fast | 1145800 | 1109000 | 1087100 | 1072100 | 1054400 | 853900 | 736600 | 662900 | 613800 | 583800 | 512900 | 510100 | 507400 | 504700 | 503300 | 500600 | 497900 | 496500 | 495100 | 492400
Battery - 2hrs | Double Bubble | Fast | 1145800 | 1109000 | 1087100 | 1072100 | 1054400 | 853900 | 736600 | 662900 | 613800 | 583800 | 512900 | 510100 | 507400 | 504700 | 503300 | 500600 | 497900 | 496500 | 495100 | 492400
Battery - 4hrs | Groundhog Day | Expected | 1808900 | 1750800 | 1716300 | 1692700 | 1664700 | 1348100 | 1162900 | 1046600 | 969100 | 921700 | 809700 | 805400 | 801100 | 796800 | 794600 | 790300 | 786000 | 783900 | 781700 | 777400
Battery - 4hrs | Cast Away | Expected | 1808900 | 1750800 | 1716300 | 1692700 | 1664700 | 1348100 | 1162900 | 1046600 | 969100 | 921700 | 809700 | 805400 | 801100 | 796800 | 794600 | 790300 | 786000 | 783900 | 781700 | 777400
Battery - 4hrs | Techtopia | Fast | 1808900 | 1750800 | 1716300 | 1692700 | 1664700 | 1348100 | 1162900 | 1046600 | 969100 | 921700 | 809700 | 805400 | 801100 | 796800 | 794600 | 790300 | 786000 | 783900 | 781700 | 777400
Battery - 4hrs | Double Bubble | Fast | 1808900 | 1750800 | 1716300 | 1692700 | 1664700 | 1348100 | 1162900 | 1046600 | 969100 | 921700 | 809700 | 805400 | 801100 | 796800 | 794600 | 790300 | 786000 | 783900 | 781700 | 777400
OCGT | Groundhog Day | Expected | 1295927.7876 | 1294503.8868 | 1291652.8747 | 1290228.9775 | 1287377.9618 | 1285954.0683 | 1283103.0488 | 1281679.159 | 1280255.2691 | 1277404.2423 | 1275980.3562 | 1273129.3256 | 1271705.4432 | 1270281.5608 | 1267430.5228 | 1266006.6442 | 1263155.6023 | 1261731.7275 | 1260307.8526 | 1257456.8032
OCGT | Cast Away | Expected | 1295927.7876 | 1294503.8868 | 1291652.8747 | 1290228.9775 | 1287377.9618 | 1285954.0683 | 1283103.0488 | 1281679.159 | 1280255.2691 | 1277404.2423 | 1275980.3562 | 1273129.3256 | 1271705.4432 | 1270281.5608 | 1267430.5228 | 1266006.6442 | 1263155.6023 | 1261731.7275 | 1260307.8526 | 1257456.8032
OCGT | Techtopia | Fast | 1295927.7876 | 1294503.8868 | 1291652.8747 | 1290228.9775 | 1287377.9618 | 1285954.0683 | 1283103.0488 | 1281679.159 | 1280255.2691 | 1277404.2423 | 1275980.3562 | 1273129.3256 | 1271705.4432 | 1270281.5608 | 1267430.5228 | 1266006.6442 | 1263155.6023 | 1261731.7275 | 1260307.8526 | 1257456.8032
OCGT | Double Bubble | Fast | 1295927.7876 | 1294503.8868 | 1291652.8747 | 1290228.9775 | 1287377.9618 | 1285954.0683 | 1283103.0488 | 1281679.159 | 1280255.2691 | 1277404.2423 | 1275980.3562 | 1273129.3256 | 1271705.4432 | 1270281.5608 | 1267430.5228 | 1266006.6442 | 1263155.6023 | 1261731.7275 | 1260307.8526 | 1257456.8032
CCGT | Groundhog Day | Expected | 1570119.1363 | 1567677.0665 | 1565234.9966 | 1562792.9268 | 1560350.857 | 1557908.7872 | 1555466.7174 | 1553024.6475 | 1550582.5777 | 1548140.5079 | 1545698.4381 | 1543256.3683 | 1540814.2984 | 1538372.2286 | 1535930.1588 | 1533488.089 | 1531046.0191 | 1528603.9493 | 1526161.8795 | 1523719.8097
CCGT | Cast Away | Expected | 1570119.1363 | 1567677.0665 | 1565234.9966 | 1562792.9268 | 1560350.857 | 1557908.7872 | 1555466.7174 | 1553024.6475 | 1550582.5777 | 1548140.5079 | 1545698.4381 | 1543256.3683 | 1540814.2984 | 1538372.2286 | 1535930.1588 | 1533488.089 | 1531046.0191 | 1528603.9493 | 1526161.8795 | 1523719.8097
CCGT | Techtopia | Fast | 1570119.1363 | 1567677.0665 | 1565234.9966 | 1562792.9268 | 1560350.857 | 1557908.7872 | 1555466.7174 | 1553024.6475 | 1550582.5777 | 1548140.5079 | 1545698.4381 | 1543256.3683 | 1540814.2984 | 1538372.2286 | 1535930.1588 | 1533488.089 | 1531046.0191 | 1528603.9493 | 1526161.8795 | 1523719.8097
CCGT | Double Bubble | Fast | 1570119.1363 | 1567677.0665 | 1565234.9966 | 1562792.9268 | 1560350.857 | 1557908.7872 | 1555466.7174 | 1553024.6475 | 1550582.5777 | 1548140.5079 | 1545698.4381 | 1543256.3683 | 1540814.2984 | 1538372.2286 | 1535930.1588 | 1533488.089 | 1531046.0191 | 1528603.9493 | 1526161.8795 | 1523719.8097
Flexible gas | Groundhog Day | Expected | 1420480 | 1418275.2756 | 1416070.5512 | 1413865.8268 | 1411661.1024 | 1409456.378 | 1407251.6535 | 1405046.9291 | 1402842.2047 | 1400637.4803 | 1398432.7559 | 1396228.0315 | 1394023.3071 | 1391818.5827 | 1389613.8583 | 1387409.1339 | 1385204.4094 | 1382999.685 | 1380794.9606 | 1378590.2362
Flexible gas | Cast Away | Expected | 1420480 | 1418275.2756 | 1416070.5512 | 1413865.8268 | 1411661.1024 | 1409456.378 | 1407251.6535 | 1405046.9291 | 1402842.2047 | 1400637.4803 | 1398432.7559 | 1396228.0315 | 1394023.3071 | 1391818.5827 | 1389613.8583 | 1387409.1339 | 1385204.4094 | 1382999.685 | 1380794.9606 | 1378590.2362
Flexible gas | Techtopia | Fast | 1420480 | 1418275.2756 | 1416070.5512 | 1413865.8268 | 1411661.1024 | 1409456.378 | 1407251.6535 | 1405046.9291 | 1402842.2047 | 1400637.4803 | 1398432.7559 | 1396228.0315 | 1394023.3071 | 1391818.5827 | 1389613.8583 | 1387409.1339 | 1385204.4094 | 1382999.685 | 1380794.9606 | 1378590.2362
Flexible gas | Double Bubble | Fast | 1420480 | 1418275.2756 | 1416070.5512 | 1413865.8268 | 1411661.1024 | 1409456.378 | 1407251.6535 | 1405046.9291 | 1402842.2047 | 1400637.4803 | 1398432.7559 | 1396228.0315 | 1394023.3071 | 1391818.5827 | 1389613.8583 | 1387409.1339 | 1385204.4094 | 1382999.685 | 1380794.9606 | 1378590.2362
Solar PV | Groundhog Day | Expected | 1175000 | 1115093.9177 | 1107923.8179 | 1100753.7182 | 1093583.6184 | 1086413.5186 | 1079243.4188 | 1072073.319 | 1064903.2193 | 1024542.4558 | 984181.6924 | 950244.3927 | 918432.7554 | 882355.1499 | 850549.3248 | 821925.0686 | 795411.3567 | 781351.055 | 763180.1002 | 743974.2434
Solar PV | Cast Away | Expected | 1175000 | 1115093.9177 | 1107923.8179 | 1100753.7182 | 1093583.6184 | 1086413.5186 | 1079243.4188 | 1072073.319 | 1064903.2193 | 1024542.4558 | 984181.6924 | 950244.3927 | 918432.7554 | 882355.1499 | 850549.3248 | 821925.0686 | 795411.3567 | 781351.055 | 763180.1002 | 743974.2434
Solar PV | Techtopia | Fast | 1218000 | 1168030.7692 | 1118061.5385 | 1075655.8742 | 972017.6307 | 882673.8175 | 856505.6085 | 832406.9748 | 809340.2755 | 796462.156 | 770282.6161 | 760419.8426 | 748553.7332 | 732648.209 | 725773.4939 | 707828.5449 | 704899.5992 | 695040.8635 | 690146.2095 | 679285.5396
Solar PV | Double Bubble | Fast | 1218000 | 1168030.7692 | 1118061.5385 | 1075655.8742 | 972017.6307 | 882673.8175 | 856505.6085 | 832406.9748 | 809340.2755 | 796462.156 | 770282.6161 | 760419.8426 | 748553.7332 | 732648.209 | 725773.4939 | 707828.5449 | 704899.5992 | 695040.8635 | 690146.2095 | 679285.5396
Wind | Groundhog Day | Expected | 1849730.2359 | 1831870.63 | 1816069.7408 | 1800411.1474 | 1786768.9013 | 1773248.2965 | 1762629.2143 | 1752103.8381 | 1741670.934 | 1731329.2895 | 1721077.7132 | 1710009.1001 | 1687223.6631 | 1658235.2159 | 1648472.8086 | 1638793.6193 | 1629196.5893 | 1619680.6777 | 1610244.861 | 1600013.1457
Wind | Cast Away | Expected | 1849730.2359 | 1831870.63 | 1816069.7408 | 1800411.1474 | 1786768.9013 | 1773248.2965 | 1762629.2143 | 1752103.8381 | 1741670.934 | 1731329.2895 | 1721077.7132 | 1710009.1001 | 1687223.6631 | 1658235.2159 | 1648472.8086 | 1638793.6193 | 1629196.5893 | 1619680.6777 | 1610244.861 | 1600013.1457
Wind | Techtopia | Fast | 1877927.3431 | 1862797.6022 | 1847804.6462 | 1811021.7391 | 1789809.2468 | 1765018.04 | 1745135.5373 | 1724498.097 | 1714188.1109 | 1690165.6866 | 1675539.4799 | 1660130.3617 | 1645760.8422 | 1629709.8662 | 1614696.0755 | 1601598.4953 | 1592160.877 | 1581038.2737 | 1572643.8147 | 1561696.3923
Wind | Double Bubble | Fast | 1877927.3431 | 1862797.6022 | 1847804.6462 | 1811021.7391 | 1789809.2468 | 1765018.04 | 1745135.5373 | 1724498.097 | 1714188.1109 | 1690165.6866 | 1675539.4799 | 1660130.3617 | 1645760.8422 | 1629709.8662 | 1614696.0755 | 1601598.4953 | 1592160.877 | 1581038.2737 | 1572643.8147 | 1561696.3923
Storage - 10 hrs | Groundhog Day | Expected | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000
Storage - 10 hrs | Cast Away | Expected | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000
Storage - 10 hrs | Techtopia | Fast | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000
Storage - 10 hrs | Double Bubble | Fast | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000

## New entrant params
New entrant technology parameters
Real June 2019 AUD
Source: | 2019 AEMO ISP Input and Assumptions workbook adjusted for WA inputs and pricing in recent developments.
Storage parameters based on industry consultation on compressed air and pumped hydro storage parameters.
OCGT FOM taken from AEMO Calculation Spreadsheet for Benchmark Reserve Capacity Price
https://www.aemo.com.au/-/media/Files/Electricity/WEM/Reserve_Capacity_Mechanism/BRCP/2020/2020-BRCP-calculation-spreadsheet-draft-report.xlsx
Technology | Scenario | Economic life (years) | Technical life (years) | Auxiliaries / self load (%) | Heat rate (GJ/MWh) | FOM ($/MW) | VOM ($/MWh sent-out) | Round-trip efficiency | Maximum depth of discharge | Storage size degradation (%, annually)
OCGT | Groundhog Day | 25 | 30 | 1.53% | 11.75 | 13502.94 | 13.803 | - | - | -
OCGT | Cast Away | 25 | 30 | 1.53% | 11.75 | 13502.94 | 13.803 | - | - | -
OCGT | Techtopia | 25 | 30 | 1.53% | 11.75 | 13502.94 | 13.803 | - | - | -
OCGT | Double Bubble | 25 | 30 | 1.53% | 11.75 | 13502.94 | 13.803 | - | - | -
CCGT | Groundhog Day | 25 | 30 | 2.51% | 7.58 | 13545 | 9.6621 | - | - | -
CCGT | Cast Away | 25 | 30 | 2.51% | 7.58 | 13545 | 9.6621 | - | - | -
CCGT | Techtopia | 25 | 30 | 2.51% | 7.58 | 13545 | 9.6621 | - | - | -
CCGT | Double Bubble | 25 | 30 | 2.51% | 7.58 | 13545 | 9.6621 | - | - | -
Flexible gas | Groundhog Day | 25 | 30 | 1.53% | 8.5 | 23000 | 9.6621 | - | - | -
Flexible gas | Cast Away | 25 | 30 | 1.53% | 8.5 | 23000 | 9.6621 | - | - | -
Flexible gas | Techtopia | 25 | 30 | 1.53% | 8.5 | 23000 | 9.7 | - | - | -
Flexible gas | Double Bubble | 25 | 30 | 1.53% | 8.5 | 23000 | 9.6621 | - | - | -
Solar PV | Groundhog Day | 25 | 30 | 2% | - | 18627.6 | 0 | - | - | -
Solar PV | Cast Away | 25 | 30 | 2% | - | 21660 | 0 | - | - | -
Solar PV | Techtopia | 25 | 30 | 2% | - | 15595.2 | 0 | - | - | -
Solar PV | Double Bubble | 25 | 30 | 2% | - | 15595.2 | 0 | - | - | -
Wind | Groundhog Day | 25 | 30 | 2% | - | 46465.8 | 3.4959 | - | - | -
Wind | Cast Away | 25 | 30 | 2% | - | 54030 | 4.065 | - | - | -
Wind | Techtopia | 25 | 30 | 2% | - | 38901.6 | 2.9268 | - | - | -
Wind | Double Bubble | 25 | 30 | 2% | - | 38901.6 | 2.9268 | - | - | -
Battery - 2hrs | Groundhog Day | 15 | 15 | - | - | 10320 | - | 81% | 80% | 1%
Battery - 2hrs | Cast Away | 15 | 15 | - | - | 12000 | - | 81% | 80% | 1%
Battery - 2hrs | Techtopia | 15 | 15 | - | - | 8640 | - | 81% | 80% | 1%
Battery - 2hrs | Double Bubble | 15 | 15 | - | - | 8640 | - | 81% | 80% | 1%
Battery - 4hrs | Groundhog Day | 15 | 15 | - | - | 10320 | - | 81% | 80% | 1%
Battery - 4hrs | Cast Away | 15 | 15 | - | - | 12000 | - | 81% | 80% | 1%
Battery - 4hrs | Techtopia | 15 | 15 | - | - | 8640 | - | 81% | 80% | 1%
Battery - 4hrs | Double Bubble | 15 | 15 | - | - | 8640 | - | 81% | 80% | 1%
Storage - 10 hrs | Groundhog Day | 40 | 40 | - | - | 37500 | - | 67% | 90% | 0%
Storage - 10 hrs | Cast Away | 40 | 40 | - | - | 37500 | - | 67% | 90% | 0%
Storage - 10 hrs | Techtopia | 40 | 40 | - | - | 37500 | - | 67% | 90% | 0%
Storage - 10 hrs | Double Bubble | 40 | 40 | - | - | 37500 | - | 67% | 90% | 0%

## Indicative LCOE comparisons
Indicative levelised cost of energy for new technologies
Real June 2019 AUD/MWh
Technology capacity factors are indicative and not an input assumption to the model.
Calculation excludes connection CAPEX, locational factors and variable fuel transport costs.
WACC
6% | <- User input
Scenario
100% | <- User input
Technology | Capacity factor
Battery - 2hrs | 6.7% | <- User input
Battery - 4hrs | 9.5% | <- User input
CCGT | 70% | <- User input
OCGT | 15% | <- User input | [6 empty] | Fuel price (AUD/GJ)
Flexible gas | 50% | <- User input | [6 empty] | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Solar PV | 24% | <- User input |  |  |  | Fuel price trajectory |  | GSOO (Base) | 5.9162 | 6.0698 | 6.3258 | 6.4794 | 6.5306 | 6.5818 | 6.6331 | 6.6843 | 6.7355 | 6.7355 | 6.7867 | 6.8379 | 7.5547 | 8.2716 | 8.2716 | 8.2716 | 8.2716 | 8.2716 | 8.2716 | 8.2716
Wind | 46% | <- User input
Storage - 10hrs | 12% | <- User input
[9 empty] | Fuel price (AUD/GJ) 2020-21: LCOE (AUD/MWh) | CAPEX (AUD/MW)
LCOE ($/MWh) | Label | Technology | Scenario | Economic lifetime (years) | FOM ($/MW) | VOM ($/MWh sent-out) | Capacity factor | Heat rate (GJ/MWh) | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
_ | Battery - 2hrs - Groundhog Day | Battery - 2hrs | Groundhog Day | 15 | 10320 | 0 | 6.7% | - | 218.5898 | 212.134 | 208.2921 | 205.6607 | 202.5556 | 167.3821 | 146.8043 | 133.8752 | 125.2616 | 119.9987 | 107.5608 | 107.0696 | 106.596 | 106.1223 | 105.8767 | 105.4031 | 104.9294 | 104.6838 | 104.4382 | 103.9645 | 1145800 | 1109000 | 1087100 | 1072100 | 1054400 | 853900 | 736600 | 662900 | 613800 | 583800 | 512900 | 510100 | 507400 | 504700 | 503300 | 500600 | 497900 | 496500 | 495100 | 492400
_ | Battery - 4hrs - Groundhog Day | Battery - 4hrs | Groundhog Day | 15 | 10320 | 0 | 9.5% | - | 236.2045 | 229.0161 | 224.7476 | 221.8278 | 218.3635 | 179.1926 | 156.279 | 141.89 | 132.3014 | 126.4369 | 112.5798 | 112.0478 | 111.5158 | 110.9838 | 110.7116 | 110.1796 | 109.6476 | 109.3878 | 109.1156 | 108.5836 | 1808900 | 1750800 | 1716300 | 1692700 | 1664700 | 1348100 | 1162900 | 1046600 | 969100 | 921700 | 809700 | 805400 | 801100 | 796800 | 794600 | 790300 | 786000 | 783900 | 781700 | 777400
_ | CCGT - Groundhog Day | CCGT | Groundhog Day | 25 | 13545 | 9.5073 | 70% | 7.58 | 76.5911 | 77.7244 | 79.6339 | 80.7671 | 81.1241 | 81.481 | 81.838 | 82.195 | 82.552 | 82.5208 | 82.8778 | 83.2348 | 88.6374 | 94.0401 | 94.0089 | 93.9777 | 93.9466 | 93.9154 | 93.8843 | 93.8531 | 1570119.1363 | 1567677.0665 | 1565234.9966 | 1562792.9268 | 1560350.857 | 1557908.7872 | 1555466.7174 | 1553024.6475 | 1550582.5777 | 1548140.5079 | 1545698.4381 | 1543256.3683 | 1540814.2984 | 1538372.2286 | 1535930.1588 | 1533488.089 | 1531046.0191 | 1528603.9493 | 1526161.8795 | 1523719.8097
_ | OCGT - Groundhog Day | OCGT | Groundhog Day | 25 | 13502.94 | 13.5837 | 15% | 11.75 | 170.526 | 172.2462 | 175.0847 | 176.8049 | 177.2368 | 177.7537 | 178.1856 | 178.7025 | 179.2193 | 179.0496 | 179.5665 | 179.9984 | 188.3367 | 196.6751 | 196.5054 | 196.4206 | 196.2509 | 196.1661 | 196.0813 | 195.9116 | 1295927.7876 | 1294503.8868 | 1291652.8747 | 1290228.9775 | 1287377.9618 | 1285954.0683 | 1283103.0488 | 1281679.159 | 1280255.2691 | 1277404.2423 | 1275980.3562 | 1273129.3256 | 1271705.4432 | 1270281.5608 | 1267430.5228 | 1266006.6442 | 1263155.6023 | 1261731.7275 | 1260307.8526 | 1257456.8032
| Flexible gas - Groundhog Day | Flexible gas | Groundhog Day | 25 | 23000 | 9.6621 | 50% | 8.5 | 90.5706 | 91.8369 | 93.9737 | 95.2401 | 95.6359 | 96.0318 | 96.4277 | 96.8235 | 97.2194 | 97.18 | 97.5759 | 97.9717 | 104.0257 | 110.0796 | 110.0402 | 110.0008 | 109.9615 | 109.9221 | 109.8827 | 109.8433 | 1420480 | 1418275.2756 | 1416070.5512 | 1413865.8268 | 1411661.1024 | 1409456.378 | 1407251.6535 | 1405046.9291 | 1402842.2047 | 1400637.4803 | 1398432.7559 | 1396228.0315 | 1394023.3071 | 1391818.5827 | 1389613.8583 | 1387409.1339 | 1385204.4094 | 1382999.685 | 1380794.9606 | 1378590.2362
_ | Solar PV - Groundhog Day | Solar PV | Groundhog Day | 25 | 18627.6 | 0 | 24% | - | 52.5799 | 50.3509 | 50.0841 | 49.8173 | 49.5505 | 49.2838 | 49.017 | 48.7502 | 48.4834 | 46.9816 | 45.4799 | 44.2171 | 43.0335 | 41.6911 | 40.5076 | 39.4426 | 38.4561 | 37.9329 | 37.2568 | 36.5422 | 1175000 | 1115093.9177 | 1107923.8179 | 1100753.7182 | 1093583.6184 | 1086413.5186 | 1079243.4188 | 1072073.319 | 1064903.2193 | 1024542.4558 | 984181.6924 | 950244.3927 | 918432.7554 | 882355.1499 | 850549.3248 | 821925.0686 | 795411.3567 | 781351.055 | 763180.1002 | 743974.2434
_ | Wind - Groundhog Day | Wind | Groundhog Day | 25 | 46465.8 | 3.44 | 46% | - | 50.88 | 50.5333 | 50.2265 | 49.9225 | 49.6577 | 49.3952 | 49.1891 | 48.9848 | 48.7822 | 48.5815 | 48.3824 | 48.1676 | 47.7252 | 47.1625 | 46.973 | 46.7851 | 46.5988 | 46.414 | 46.2308 | 46.0322 | 1849730.2359 | 1831870.63 | 1816069.7408 | 1800411.1474 | 1786768.9013 | 1773248.2965 | 1762629.2143 | 1752103.8381 | 1741670.934 | 1731329.2895 | 1721077.7132 | 1710009.1001 | 1687223.6631 | 1658235.2159 | 1648472.8086 | 1638793.6193 | 1629196.5893 | 1619680.6777 | 1610244.861 | 1600013.1457
_ | Storage - 10hrs - Groundhog Day | Storage - 10hrs | Groundhog Day | 25 | 18627.6 | 0 | 12% | - | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 240.9701 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000

## Candidate technologies by zone
Candidate technologies by zone
This sheet contains the list of new entrant candidate technologies at each zone. Bespoke new entrant candidates will be considered individually.
"No" indicates that a technology is not considered a candidate at that zone.
zone | OCGT | CCGT | Flexible gas | Solar PV | Wind | Battery - 2hrs | Battery - 4hrs | Storage
NC | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
MW | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
NB | Yes | Yes | Yes | Yes | No | Yes | Yes | No
MN | Yes | Yes | Yes | No | No | Yes | Yes | No
MT | No | No | No | No | No | Yes | Yes | No
MS | Yes | Yes | Yes | Yes | No | Yes | Yes | No
ME | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
EC | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
EG | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
SW | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
SE | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No

## Conn CAPEX by zone
Connection CAPEX cost multipliers by zone
This sheet contains locality factors which vary depending on the zone that the generation is connected to.
The locality factors will be directly multiplied to the connection cost.
zone | Factor
NC | 1.1
MW | 1.25
NB | 1.1
MN | 1
MT | 1
MS | 1
ME | 1.2
EC | 1.2
EG | 1.35
SW | 1.07
SE | 1.15

## Wind capacity factors
Representative nodal wind farm capacity factors
Existing wind generators are modelled with capacity factors according to past performance.
zone | Capacity factor (new entrants)
NC | 46%
MW | 44%
NB | -
MN | -
MT | -
MS | -
ME | 38%
EC | 38%
EG | 42%
SW | 42%
SE | 44%