## Sheet1
Issue | Ref. TR Review | Summary Issue/ Proposed solution | Notes
Transmission voltage limits | 3.4 | Clarification of transmission voltage limits – a new timeframe approach for returning to steady state voltages after a disturbance and has separated voltage limit requirements across operational and planning timescales. | Consultation will focus on any implications arising from Western Power’s selected technical limits and the inclusion of ‘economic efficiencies’ in clause 2.2.2.7(c).
Distribution voltage limits | 3.5 | Distribution voltage limits can be clearer and align with wider limits adopted in other jurisdictions. | Will consult on updated proposal
Note: since the time of the submission in Sep 2023 there have been changes to the Australian Standards. The revised proposal is to adopt the limits in AS IEC 60038: 2022 voltage standard, which stipulates a voltage supply range of +/- 10% under normal operating conditions.
Standard for transient stability | 3.6 | Standard for transient stability is technology specific (rotor angle) and need to be more clearly applicable to inverter technologies.
Standard for oscillations | 3.7 | Standard for oscillations does not consider all forms of oscillation. Adequately Damped is not defined in WEMR or TR.
Voltage stability | 3.8 | Lack of clarity on assessing voltage stability- amendments to address voltage stability requirements.
Network Service Provider obligations - stability and modelling | 3.9 | Provide a definitive obligation for Western Power to maintain the existing load and generator modelling guidelines, and to place clear obligations on Western Power to make appropriate assessment of system stability while avoiding unnecessarily prescriptive requirements regarding how the stability assessments are to be made
Network Service Provider obligations - power system performance | 3.11 | Inclusion of a specific clause for the Network Service Provider to ensure sufficient monitoring is in place
Network Service Provider obligations - system restart | 3.12 | Inclusion of specific clauses that that places obligations on Western Power to assist with, and facilitate, the system restart plan
UFLS requirements | 3.13 | Replacing the prescriptive arrangements with a high-level obligation on the NSP to provide a UFLS scheme and coordinate the functional design with AEMO and specifying that the NSP may require a User to make a portion of their load available for UFLS. | Western Powers obligation to analyse and understand if the UFLS system meets required outcomes in support of AEMO's development of UFLS requirements will be considered. Work will continue between EPWA, AEMO and Western Power to arrive at the right level of regulatory specification, noting that the framework will need to be harmonised under the ESMR.
Transmission planning criteria | 4.1 | Variety of changes, including RRST may no longer be able to be designed to meet the NCR criteria. Proposal to implement a hybrid solution which includes changes to the TSP Criteria to introduce a new Demand Group Structure and move towards risk-based or probabilistic techniques. | The matters in section 4.1 form part of the Transmission Planning Criteria, which are being considered in detail under the PSSR Standards Review. EPWA will incorporate the issues raised in section 4.1 of the Technical Rules Submission as part of the planning criteria section of the consultation paper.
Def. of credible contingency | 4.2 | Definition of credible contingency to be clearer and take into account the change in certainty over the infrastructure planning, implementation and operation time horizons. | The proposal is predicated on the ongoing separation between the WEM Rules and the Technical Rules. Given that both will be harmonised into the ESMR, consideration will be given to the harmonisation of the credible contingency frameworks.
Def. of plant ratings to adopt cyclic or short-term ratings | 4.3 | Use of alternative plant ratings within planning timescales. Proposal to update the transmission planning criteria to explicitly allow the use of alternative or short-term ratings when determining compliance with planning criteria, but only include high level description. | Consultation will focus on potential impacts of the market of the proposed changes.
Duration of protection equipment being taken out of service. | 5.3 | Duration of protection equipment being taken out of service - WP has proposed the removal of the six-month limit on outages.
Definition of equipment for which CFCTs apply | 5.4 | Application of maximum total fault clearance times for ‘new’ and ‘existing’ equipment – proposal to use guideline to capture appropriate guidance. | Consideration will need to be given to whether a Guideline is the most appropriate instrument under the ESMR for these matters.
Weak infeed assessments under islanding conditions | 5.5 | Clarifications to limit weak infeed assessments to high-risk sustained islanding scenarios, exclude circuit breaker failures, and define a practical point of assessment within the network.
Distinction between transmission and distribution protection operation for critical fault clearance times | 5.6 | Changes to align transmission and distribution protection operation for critical fault clearance times.
Review of user control and protection settings. System design and construction standards | 6.2.6, 6.2.7 | Proposed amendments relating to Control and Protections settings and System design and construction standards.
Aligning protection and disturbance ride-through requirements. | 6.8.6 | Changes to ensure consistency with generating system protection requirements and disturbance ride through requirements between the WEM Rules and Technical Rules.
Alignment with revisions to network planning criteria and network service provider obligations | 8.3 | Adjustment to the Technical Rules to take into account other revisions made to Chapter 5 in the Technical Rules submission
Clarifying arrangements for planning network outages | 8.5 | Inclusion of obligations for the Network Service Provider to develop an outage assessment guideline.
Clarifying acceptable timeframes for protection outages | 8.9 | Inclusion of a clause that requires the Transmission Network Operator to consider the availability requirements specified in clause 2.9.3 when assessing the impact of transmission equipment protection outages
Wording of voltage control can be improved. | 8.10 | Adequate consideration of all expected load conditions - proposal for the operational requirement to be specified in a manner that caters for all expected load conditions.